Tender text Bello Zon series CDVc

Hint on use of the Or: -positions:

Every Or: -position represents a feature, which has to be selected for a certain type of Bello Zon CDVc. All further Or: -positions have to be erased.

Feature “Wide range power supply” can not be combined with feature “reactor housing with suction device” and with by-pass features “with by-pass pump 230 V” or “for filling of an intermediate storage tank with solenoid valve 230 V”.

Feature “Power supply 100-115 V” can not be combined with by-pass-feature “with by-pass pump 230 V” or “for filling of an intermediate storage tank with solenoid valve 230 V”.

Control versions with measurement and control have to be combined with 0/4-20 mA-inputs.

Chlorine dioxide system Bello Zon CDVc serving production, metering and monitoring of chlorine dioxide according to the chlorite-acid-procedure. Highest operating safety thanks to online stroke length-monitoring of the pumps for the chemical precursors.

Reactor and reactor outlet valve made of highly resistant and enduring PVDF.

Central controller with large 5,7’’ colour screen for displaying operational information and advices for the menu-driven handling in plaintext. Automatic surveillance of all operating parameters and of servicing dates.

Type: CDVc 20

Capacity: 1-20 g/h, min. 6,4 g/day

Operating pressure: max. 8 bar

Operating temperature: 10-40 °C

Dimensions (HxWxD): 1344 x 1002 x 200 mm

Weight: ca. 26 kg

Or:

Type: CDVc 45

Capacity: 2-45 g/h, min. 16 g/day

Operating pressure: max. 8 bar

Operating temperature: 10-40 °C

Dimensions (HxWxD): 1344 x 1002 x 200 mm

Weight: ca. 27 kg

Or:

Type: CDVc 120

Capacity: 6-120 g/h, min. 40 g/day

Operating pressure: max. 8 bar

Operating temperature: 10-40 °C

Dimensions (HxWxD): 1344 x 1002 x 200 mm

Weight: ca. 28 kg

Or:

Type: CDVc 240

Capacity: 12-240 g/h, min. 80 g/day

Operating pressure: max. 8 bar

Operating temperature: 10-40 °C

Dimensions (HxWxD): 1342 x 1000 x 248 mm

Weight: ca. 45 kg

Or:

Type: CDVc 600

Capacity: 30-600 g/h, min. 140 g/day

Operating pressure: max. 8 bar

Operating temperature: 15-40 °C

Dimensions (HxWxD): 1711 x 1200 x 273 mm

Weight: ca. 75 kg

Or:

Type: CDVc 2000

Capacity: 100-2000 g/h, min. 470 g/day

Operating pressure: max. 5 bar

Operating temperature: 15-40 °C

Dimensions (HxWxD): 1900 x 1400 x 370 mm

Weight: ca. 120 kg

The system is assembled on a plastic wallplate ready for connection. Hydraulic connection, power supply and electric control in-/outputs have to be built up on site. The system offers the following features:

Wide range power supply 100-230 V +/- 10 %, 50/60 Hz

Or:

Power supply 230 V +/- 10 %, 50/60 Hz

Or:

Power supply 100-115 V +/- 10 %, 50/60 Hz

Without bypass piping.

Mounting dimension reactor outlet valve: G 1“ (G 2 1/4“ at type CDVc 2000).

Bypass PVC-U with float flow meter.

Input: socket joint d32

Output: screwing with socket joint d32

(d50 each at type CDVc 2000).

1 flushing assembly consisting of ball valve DN 25 (DN 40 at type CDVc 2000) and ball valve with hose clip d20 is scope of delivery and has to be assembled on site directly downstream the plant into the bypass piping.

Or:

Bypass PVC-U with float flow meter.

Input: socket joint d32

Output: screwing with socket joint d32

(d50 each at type CDVc 2000).

1 flushing assembly consisting of ball valve DN 25 (DN 40 at type CDVc 2000) and ball valve with hose clip d20 is scope of delivery and has to be assembled on site directly downstream the plant into the bypass piping.

1 stainless steel bypass pump (capacity: 0,54 kW, 2,5 cbm/h at 2 bar, mounting dimension RP 1“) is scope of delivery and has to be assembled on site directly upstream the plant into the bypass piping. Power supply and control directly out of the controller.

Or:

Bypass PVC-U with float flow meter.

Input: socket joint d32

Output: screwing with socket joint d32

(d50 each at type CDVc 2000).

1 flushing assembly consisting of ball valve DN 25 (DN 40 at type CDVc 2000) and ball valve with hose clip d20 is scope of delivery and has to be assembled on site directly downstream the plant into the bypass piping.

The bypass is designed for filling of an intermediate storage tank for ClO2-solution. For this purpose, the plant include a water supply line consisting of shut-off valve, pre-filter, pressure reducer, solenoid valve (230 V, power supply and control directly out of the controller), water meter, and needle valve, which has to be assembled on site.

Or:

Bypass PVC-U with float flow meter.

Input: socket joint d32

Output: screwing with socket joint d32

(d50 each at type CDVc 2000).

1 flushing assembly consisting of ball valve DN 25 (DN 40 at type CDVc 2000) and ball valve with hose clip d20 is scope of delivery and has to be assembled on site directly downstream the plant into the bypass piping.

The bypass is designed for filling of an intermediate storage tank for ClO2-solution. For this purpose, the plant include a water supply line consisting of shut-off valve, pre-filter, pressure reducer, solenoid valve (24 V, power supply has to be managed externally, e.g. via a separate transformer), water meter, and needle valve, which has to be assembled on site.

Calibration of the metering pumps by means of two enclosed measuring cylinders.

Or:

Calibration of the metering pumps by means of an integrated calibration device, working as a suction aid, also. Filling of the calibration device works by means of an enclosed vacuum pump.

Or:

Calibration of the metering pumps by means of two enclosed measuring cylinders.

The reactor is surrounded by a gas-tight housing, which is flushed periodically with fresh air by means of an integrated suction device. The housing is outfitted with a level switch fort he detection of leakages. The suction devices inlet (PVC screwing with socket joint DN10) has to be assembled on site with potable water supply 1-6 bar. The outlet needs a free drainage.

Or:

Calibration of the metering pumps by means of an integrated calibration device, working as a suction aid, also. Filling of the calibration device works by means of an enclosed vacuum pump.

The reactor is surrounded by a gas-tight housing, which is flushed periodically with fresh air by means of an integrated suction device. The housing is outfitted with a level switch fort he detection of leakages. The suction devices inlet (PVC screwing with socket joint DN10) has to be assembled on site with potable water supply 1-6 bar. The outlet needs a free drainage.

The connection between chemical supply and metering pumps has to be managed on site.

Or:

The chemical supply is affected by means of 2 enclosed variable suction lances for 5-60 l cans. 2 integrated level switches transmit signals to the controller for almost empty and empty chemical supply.

Or:

The chemical supply is affected by means of 2 enclosed variable suction lances for 200 l drums. 2 integrated level switches transmit signals to the controller for almost empty and empty chemical supply.

Or:

The chemical supply is affected by means of 2 enclosed flexible suction fittings up to 5 m. 2 integrated level switches transmit signals to the controller for almost empty and empty chemical supply.

Or:

The chemical supply is affected by means of 2 enclosed variable suction lances for 5-60 l cans. 2 integrated level switches transmit signals to the controller for almost empty and empty chemical supply.

2 drip pans 40 l are scope of delivery.

The operating menu is preset on English, German, French, Italian and Spanish language. Further languages can be freely adjusted.

Capacity control can be done manually, flow-dependant on a water meters signal, or by means of an external signal 0/4-20 mA (if analogue input existing).

Or:

Capacity control can be done manually, flow-dependant on a water meters signal, measurement dependant by means of the integrated measurement of ClO2, or by means of an external signal 0/4-20 mA. Chlorite can be measured additionally to the ClO2-measurement.

Or:

Capacity control can be done manually, flow-dependant on a water meters signal, measurement dependant by means of the integrated measurement of ClO2, or by means of an external signal 0/4-20 mA. Chlorite can be measured additionally to the ClO2-measurement. The measured values are documented and visualized by means of the integrated data logger and screen recorder.

Or:

In- and outputs:

2 digital inputs for leakage or external failure (e.g. gas warning device)

1 free configurable digital input for function pause or choice between two programmable dosing capacities

1 input for water meter (reed contact, hall sensor, NAMUR-signal or open collector up to 10 kHz)

4 relay outputs (alarm NC, alarm NO, warning, and operation)

Or:

In- and outputs:

2 digital inputs for leakage or external failure (e.g. gas warning device)

1 free configurable digital input for function pause or choice between two programmable dosing capacities

1 input for water meter (reed contact, hall sensor, NAMUR-signal or open collector up to 10 kHz)

2 free configurable analogue inputs 0/4-20 mA

4 relay outputs (alarm NC, alarm NO, warning, and operation)

Or:

In- and outputs:

2 digital inputs for leakage or external failure (e.g. gas warning device)

1 free configurable digital input for function pause or choice between two programmable dosing capacities

1 input for water meter (reed contact, hall sensor, NAMUR-signal or open collector up to 10 kHz)

1 free configurable analogue outputs 0/4-20 mA

4 relay outputs (alarm NC, alarm NO, warning, and operation)

Or:

In- and outputs:

2 digital inputs for leakage or external failure (e.g. gas warning device)

1 free configurable digital input for function pause or choice between two programmable dosing capacities

1 input for water meter (reed contact, hall sensor, NAMUR-signal or open collector up to 10 kHz)

2 free configurable analogue inputs 0/4-20 mA

1 free configurable analogue outputs 0/4-20 mA

4 relay outputs (alarm NC, alarm NO, warning, and operation)

Integrated memory for recording of all failure messages and operator control actions. Values can be exported by means of an integrated SD-memory card.

The system meets all the requirements of the DVGW specifications W 224 and W 624 with regard to design and operation and is designed for operation with pre-diluted chemicals Bello Zon Chlorit (9 % NaClO2) and Bello Zon Acid (7,5 % HCl). The chemicals have to meet the quality requirements of DIN EN 938 and DIN EN 939. To ensure safe operation, the installation of a gas warning device is recommended, which is switching off the system in case of any leakage of chlorine dioxide. Local regulations for installation and operation of the system have to be regarded.