## Slide 1
Ammonia Package
Notes: <number>

## Slide 2: Back panel
<number>
Note: At ambient temperature Ammonia is lighter than air.

## Slide 3: Log on screen
<number>

## Slide 4: Standard sensors and outputs.
<number>

## Slide 5: Views: User test & Sensor Values
<number>
Notes: <number>
Phantom inputs may be used to log user test values. Once logged they are used identically to sensor that change in real time.
The ‘Keypress Log’ time stamps the last 25 entries including the entry of manual to test values.
More on using these manual values in subsequent slides.

## Slide 6: Plug & Play
<number>
C = pH
D = Ammonia
E = 4-20 mA out
pH
F = 4-20 mA out
Ammonia
G = Temperature
Sensor
ProMinent pt100
Gain = 0.1197
Off = -19.4725
Notes: <number>
Input ‘A’ is hardwired as a conductivity sensor, Input ‘B’ as a temperature sensor and Input ‘G’ as a 4-20mA input.
Most controllers measure conductivity & all but boiler blowdown have temperature compensation. This is the lowest cost way of delivering these sensor services.
Inputs C-D and E-F can be single or dual sensor cards and/or single/dual 4-20mA output cards.
Cards may be CT=Cond. Temp, OP:ORP-pH, B=Boiler Cond, CI:4-20mA input, CR:Corrosion Rate, IO=4-20mA output:
When you plug a card in, the controller correctly configures the input for the sensor type. Some cards have selection/range jumpers, read by the controller.
If you remove or change a sensor card & the sensor(s) on the previous card were used for control or compensation, the controller removes the unavailable sensors.
Sensor cards may be used on both MultiFlex & Aegis controllers without modification. Aegis controllers don’t recognize MultiFlex Rate-Stroke cards.
Power OFF. Remove or socket a new card. Power ON & you’re done.

## Slide 7: Log-in
<number>
Notes: <number>
There are 3 types of users: Operate: setpoints, calibrate, prime, Configure: modify feed modes, pump type, controls. admin: System settings, units, IP, View-Config selection.
All logged in users can view everything. If you attempt to modify above your permission level you get advice telling you the required permission level.
Support: You can always view the controller serial number and any active alarms. The default passwords are the same as the MultiFlex.
Once logged in a user can change their password & user id. The default permissions – access levels are displayed in this slide.
The admin user can change any user’s permission level but cannot view their password. Important, since activity is logged by user id.
Like the other Aquatrac controllers, if your support controller’s running the password reset firmware, you can modify your S/N to match the end-users S/N to generate a Reset Password. Logon with to reset Password to return all passwords to the factory default.

## Slide 8: Sensor Diagnostic
<number>
Notes: <number>
When calibrate a sensor the controller adjusts the sensor OFFSET or GAIN to make the measured millivolt level display your calibration value.
When you select a sensor link, you’ll view the Diagnostic page and you’ll be able to see the separation between the current sensor offset & gain and the factory default.
All sensors but 4-20mA inputs are single point calibrated; Conductivity calibration modifies GAIN. Sensors like pH, ORP, Temperature, modify OFFSET.
Status flags you on alarms & calibration problems
The controller logs sensor MIN.MAX & AVERAGE. Range within the log period varies with both sensor type & the state of the control cycle…. Conductivity will fall when the bleed’s ON.
Compensation varies with sensor type. Non-boiler conductivities are always thermally compensated. pH is seldom thermally compensated since the effect on typical temperature range is insignificant.
Sensor Compensation may be None, Corrosion, Calculate ppm, Rate-to-Volume, Inventory …
Input card ID is used to the controller configure Sensor drivers.

## Slide 9: Sensor Compensation
<number>
Notes: <number>
You can modify the name of the sensor. HTML characters are auto-blocked.. < > &
You can override the calculated calibration OFFSET & GAIN. Support: Set GAIN = 0 & OFFSET = Desired Sensor Value. Handy for demos, verifying control response & isolating a sensor from its control.
You control the digits after the decimal point. pH = 2 & you can see the tower cycle up. Inventory = 3 & you can effect pumping mL (10mL about 0.003 Gallons).
A single temperature input can be used to compensate more than one sensor, for control, to generate alarms…
The default thermal compensation rate works for typical cooling waters. If you don’t compensate a 10F change in water temperature is 10% conductivity measure error. 150uS @ 1500uS setpoint.
Don’t mention TDS unless queried. Conductivity tracks TDS if the conductivity is thermally compensated. It ain’t technically correct but it’s convention in our business. Yes you can set units = ppm (TDS) since one multiplier works for most towers but you’ll get calibration errors.

## Slide 10: 4-20mA Outputs
<number>
Notes: <number>
Variable frequency removes the need for 4-20mA pump control. Still used occasionally for monitoring & legacy controls. Rarely you’ll see a 4-20mA tower blowdown valve. Don’t do a proportional valve boiler blowdown.
Set to Manual to get the loop running then switch to Auto to operate. The controller remembers the setpoints in both modes. If you are controlling a pump or valve, use Manual & 0% to ensure full OFF.
If you select Auto, the page displays 4mA & 20mA setpoints and you can set which sensor A..N you wish to use for loop value.
Zero & Span are keypad adjusted.
The flowswitch interlock is not just a control utility, it’s also a way to flag an automation system that sample flow is OFF & the sensor value no longer represents the bulk process.
The current loop output is loop powered. This method has two benefits, The current loop is DC isolated & the controller can alarm on an open loop.
You can still encounter ground loops but it’s not caused by 4-20mA card which is optically isolated from the controller. But it’s still your problem to correct.

## Slide 11: System: Passwords
<number>
Notes: <number>
This page shows you your current Access Level in the Status line.
LCD users can only use passwords comprised of CAPITAL letters to keep login scrolling within patience limits.
Browser users cannot include HTML characters.
Only the current user can view & modify his or her UserID & password or you could read the slide text boxes to give your presentation immediacy.
The admin user cannot change her/his UserID. There is only one admin per controller & only they can set other users Access Level.
Note: 5 invalid passwords lock the controller out for ALL users until 7:00 AM. Bypass the lock-out by turning the control ON/OFF, unplug-Plug-in on the assumption that if you are on-site you are a legitimate user.

## Slide 12: Possible Markets
- municipal water plant chloramination monitoring
- wastewater of gas scrubbers
- wastewater monitoring
- ammonia leaks in cooling towers
- the food sector, e. g. for wine and beer
- laboratories.
<number>

## Slide 13: Chloramination
<number>

## Slide 14: Ammonia vs.pH
<number>
Only NH4+ ions (ammonium) are present at pH <7
The ratio of NH4+ ions (ammonium) to NH3 (ammonia) is 1:1 at pH 9.3
Only NH3 (ammonia) is present at pH >11
Notes: <number>
5 ON/OFF relay controls and 4 variable frequency pump controls.
Browser includes an AJAX powered real time view that auto-updates every 2 seconds. No more REFRESH button push to update.
A MultiFlex has up to 14 Analog sensor inputs and up to 12 Water Meter/Contact Set/Flowswitch inputs. An Aegis has 7 Analog sensor inputs and 8 Water Meter/Contact Set/Flowswitch inputs. The extra 6 Analog sensor inputs and 4 Meter/Contact inputs are available as ‘Phantom’ inputs used for logging Inventory, ppm, manual entry and meter summing…
Sensor driver cards are interchangeable between Aegis & MultiFlex. They’re still both Plug & Play.
The Aegis carefully limits user options to those applicable with the selected sensor and control mode. The power & flexibility are there when you need them but concealed on simple, common controls.
Feed verify, calculated ppm, inventory are standard. Volume copying, Output mirroring, contact inverting and sequential contact set controls add PLC type flexibility.
Trackster’s still used for reporting but all command & control requires only a browser, even if you are modem connected.
Frequency controls report pumped volume. Setpoints & Limits are simpler; usage tracking easier.

## Slide 15: HOCL vs. pH (Hach slide)
<number>

## Slide 16: pH Chloramines
<number>

## Slide 17: Reaction time vs. pH
<number>

## Slide 18: Chloramination Chemistry (Hach slide)
<number>
Note: Fastest formation of chloramine occurs at pH 8.3

## Slide 19: Chloramination curve (Hach slide)
<number>

## Slide 20: Chloramination curve (cont.) (Hach slide)
<number>

## Slide 21: Chloramination curve (cont.) (hach slide)
<number>

## Slide 22: Chloramination species (Hach slide)
<number>