## Slide 1: Chlorine Dioxide System Legio Zon®

## Slide 2: Basic Info
capacity: 5 or 10 g/h
operation with Bello Zon standard chemicals
  1 vol. chlorite 7.5 % + 3 vol. HCl 9% + 20 vol. water
  concentration ClO2: 2 g/l
easy operation, low maintenance effort
low price + high level technology

## Slide 3: Plant’s Design: Front
line cord
flow monitor
dosing pump chlorite
outlet chlorine dioxide
dosing pump chlorine dioxide
spring for defined back pressure
dosing pump acid
input dilution water
draining valve
controller

## Slide 4: Plant’s Design: Rear
inlet acid + chlorite
reactor
venting hose
storage tank
over-/under-pressure valve
solenoid valve dilution water
activated carbon filter
Off-gas bag
draining valve
outlet ClO2
solenoid valve ClO2

## Slide 5: Display Controller
displaying operating parameters
  time after last ClO2-preparation
  total runtime
  produced amount of ClO2-solution
  operating status such as Runtime/Pause, filling reactor, etc.
displaying failure messages in plain text
menu navigation for
  commissioning
  setting operating parameters
  maintenance
Runtime
ClO2-Production
time 04:21 h:m
Runtime
Runtime: 2127 h
ClO2: 1596 g

## Slide 6: Maintenance
controller switches off after 1 year
  maintenance and restart only possible with service code
maintenance
  menu navigation of the controller for the plant‘s flushing and draining
  exchange of diaphragms and gaskets in the dosing pumps
  exchange of the activated carbon cartridge and other wear and tear parts
  reset of hours-run and chlorine dioxide meters
  calibration of the dosing pumps
  time need: about 2 hours

## Slide 7: Technical Data (preliminary)
Capacity: 0-10 g/h
Dimensions (HxWxD): 650 x 550 x 310 mm
Weight (without hood): 48 lbs
Power supply: 115 V, 50/60 Hz
Electrical inputs: 3 (water meter, failure, pause)
Electrical outputs: 3 (operation, warning, alarm)
Service water: 87 psi max
ClO2 stock solution: 0.2 gal of 2,000 ppm