## PROMINENT PROMIX POLYMER BLENDING SYSTEM SPECIFICATIONS

Model S30-0.3T

PART 1	GENERAL

1.01	DESCRIPTION

- The polymer system shall be the standard equipment of the supplier involved in the manufacture of similar type equipment and shall be as manufactured by ProMinent Fluid Controls, Inc. Model S30-0.3T.

- Equipment included with the polymer system includes:

- Single Motor Mixing Chamber

- Dilution water controls

- Peristaltic Neat polymer pump

- System Controls

- The polymer system shall be a complete skid mounted system including all interconnecting piping and wiring.

PART 2	PRODUCTS

2.01	SYSTEM DESCRIPTION

A.	True Multi-Zone Mixing Chamber

- Polymer and water shall be mixed in a chamber designed to create sufficient mixing energy.

- The chamber shall contain a minimum of three chambers. Dual or single mixing chamber designs shall be unacceptable.

- This design shall include two motor-driven impellers that will create high fluid sheer at point of polymer and water introduction.

- Polymer solution shall undergo a tapered mixing intensity slope as it exits the initial sheer zone and passes through a second, and third mixing zones isolated by baffles.

- Each chamber shall contain Polymer activation efficiency consistent over the entire dilution water range.

- Mixing chamber shall be opaque to prevent solution degradation from ultraviolet light. Clear mixing chambers shall be unacceptable.

- Impellers shall be driven by a 1/8 HP maximum washdown duty motor.

- Motor shall be TEFC.

- Impeller speed shall be 1730 rpm, minimum.

- Motor shall be direct-coupled to impeller shafts.

B.	Dilution Water Control

- Dilution water shall be split into two streams. Primary water flow shall supply the mixing chamber.

- Secondary water flow shall be used to post dilute the activated polymer stream to desired feed concentration.

- These two streams shall be completely blended by an integrated static mixer prior to application injection point.

2.	Unit shall have an electric solenoid valve for on/off control of total dilution water flow.

- Flow indicators and flow control valves shall be provided for each dilution water stream.

- Unit shall include a pressure reducing regulator to adjust supply line pressure.

C.	Pump

- Unit shall have one neat polymer metering pump.

- Pumps shall be peristaltic (tube) pump. Positive displacement, diaphragm type, gear pumps, or progressive cavity pumps shall not be acceptable.

- Internal diameter of the pump tubing will be 5.0 or 8.0 mm.

- Polymer pump shall operate on 0-15 VDC.

- Pump Monitor will stop unit in the event of pumping tube breaks, empty chemical supply or other polymer supply interruptions.

D.	Controls

- Unit shall be controlled through an on-off-remote circuit controlled by a three-position switch.

- In the remote switch position, the unit shall accept a run signal. Unit is manually controlled in the on position.

- Unit shall accept a 4-20 mA analog signal to pace the polymer metering pump.

- Unit shall detect loss of water flow, sensing that water flow has been interrupted for any reason, will place the polymer pump and mix chamber on standby and will restart it automatically when flow is restored.

2.02	TECHNICAL DATA

A.	Connections – Plumbing

1.	Dilution water inlet, 3/4” FNPT

2.	Neat polymer inlet, Supplied Tubing

3.	Solution discharge, 3/4” FNPT

B.	Connections – Electrical

1.	Standard, grounded male plug – 120 / 1/ 60, 20 amps

2.	Plug in connection – 4-20 mA signal input

3.	Terminal blocks – dry contact input for remote start

C.	Dimensions

1.	20” wide x 18” deep x 40” high

D.	Materials of Construction

1.	PP/PE Structural frame

2.	Plumbing – PVC

3.	Mixing chamber – Polypropylene

E.	Performance

1.	Dilution water – 0 - 30 gph primary mixing

2.	Metering pump – 0.01 – 0.31 gph neat polymer

PART 3	EXECUTION

  - INSTALLATION

A.	The equipment shall be installed per the contract documents and manufacturer’s recommendations.

3.02	WARRANTY

- Polymer feed system shall be warranted for a period of 12 months from the date of start-up by authorized technician.

- Damage due to makeup water particulates will not be considered as a warranty defect and will be the responsibility of the owner.

- In addition, supplier shall warrant the system to operate in accordance with owner’s expectation and performance.

- If dissatisfied with system performance for any reason, the owner shall have the right to return the system to vendor for a refund of vendor’s sale price any time during the first 30 days following start-up.

PART 4	OPTIONAL ACCESSORIES

- Calibration cylinder: A suitably sized calibration cylinder shall be supplied for the neat polymer feed pump.  Cylinder shall be mounted to frame with PVC isolation ball valves.  Cylinder shall be calibrated in mL, and be constructed of clear PVC with slip on cap and ½ inch NPT vent connection.

- Drumstick: A rigid drumstick suitable for mounting in the neat polymer drum bunge or vent connection shall be supplied to completely evacuate the drums contents.  The drumstick shall be supplied with 2 inch NPT and ¾ inch NPT connections for connection to either port.  Drumstick construction shall be PVC.

- Drum Dryer: A desiccant drum dryer shall be supplied to eliminate moisture laden air from entering the polymer drum.  The drum dryer shall include a ¾ inch connection for mounting in the drum vent port.

- Drum Dolly : A drum dolly/cradle shall be supplied for moving drums or tipping the drum on its side for dispensing.  Polyolefin wheels and rollers shall be supplied for moving or positioning the drum, a kickstand shall be supplied to support the drum dolly in an upright position.  Drum dolly shall have a 1 inch structural pipe frame, 1000 lb. capacity and suitable coating for corrosion prevention.